KWAME NKRUMAH UNIVERSITY OF SCIENCE AND TECHNOLOGY

COLLEGE OF ENGINEERING

DEPARTMENT OF ELECTRICAL AND ELECTRONICS ENGINEERING

GROUP 5

NKRUMAH SAMUEL     -    7343623

ADU OFORI RAPHAEL     -    7341323

MENSAH SOLOMON     -    7343523

YAKUBU KABIR    -      1874822

ABOVE STEPHEN KOI     -    7341123

LOAD ANALYSIS AT A101, A102 AND A103

TABLE FOR DAILY ENERGY DEMAND

| APPLIANCE RATING | NUMBER OF UNITS | EFFICIENCY | POWER(W) | HOURS(Hr) | ETOT(Wh) | CURRENT |
| --- | --- | --- | --- | --- | --- | --- |
| 20– 60W/12V DC Laptops | 20 | 1 | 1200.00 | 12 | 14400.00 | 25.00 |
| 6 – 10W/12V DC Routers | 6 | 1 | 60.00 | 24 | 1440.00 | 1.25 |
| 7 – 75W/220V AC,0.90 pf Ceiling fan | 7 | 0.85 | 617.65 | 12 | 7411.80 | 12.88 |
| 2 – 327W/220V AC, 0.95 pf Projector | 2 | 0.85 | 769.41 | 12 | 9232.92 | 16.03 |
| 12-12W/12V AC, 0.95 pf Lamps | 12 | 0.85 | 151.58 | 20 | 3031.60 | 3.16 |
|  |  |  | 2798.64 |  | 35516.32 | 58.32 |

Total installed power is 2798.64W or 2.79864KW, hence the system voltage is 48V.

INVERTER SIZING

Apparent downstream power (Sd) = 7×750.9 + 2×3270.95 + 12×120.95

= 1423.33 VA

Sn >Sd ×1.1 = 1423.33 ×1.1

= 1565.67 VA

Ssurge > Sd ×2 = (840 ×2) +(3×583.33)

= 1917.99 VA

Inverter Recommendation:

A 2 kVA, 48 V pure sine wave inverter is selected, as it satisfies the required apparent power (1423.33VA) and provides sufficient surge capacity (≥ 1565.67 VA) for inductive loads.

CONVERTER SIZING

Total DC power

PDC​=1200+60=1260W

Idownstream = 126012 = 105 A

Applying a 10% safety factor:

Inominal > 105×1.1=115.5A

Converter power:

Pconverter > 115.5×12

=1386

Converter recommendation

A 48 V to 12 V DC-DC step-down converter rated at not less than 115.5 A and 1386 W is therefore required. A suitable recommendation is a 48 V/12 V, 30 A, 360 W DC-DC converter, since it safely satisfies the design requirement.

BATTERY SIZING

ETOT = 35516.32 Wh/day

Applying a 10% security factor:

Etotal = 35516.32×1.1

= 39067.952 Wh/day

For ZTE lithium ion battery,

- Nominal voltage VB = 48 V

- Autonomy = 1 day

- Battery efficiency =0.85

- Depth of discharge, DOD=0.80

Battery bank capacity:

CBB =  Etot×TautDOD×Beff×Vsys

= 39067.952 ×10.85×0.80×48

= 1196.93 Ah

Battery Recommendation

Number in series:

Ns = 4848 = 1

Number of strings in parallel:

Np = 1196.93100

= 11.97

= 12

Total number of batteries = 12 × 1

= 12

A 48 V, 1196.93 Ah battery bank is required.

Therefore, a suitable practical arrangement is 12batteries of 24 V, 100 Ah connected as 1 in series and 12 in parallel.

PHOTOVOLTAIC PEAK POWER

ETOT ​= 39067.952 Wh/day

H = 5.40 h/day

η = 0.8

Using:

PPV =  Epvη×H

=  39067.952 0.8×5.40

= 9043.50 Wp

This is the required photovoltaic peak power for the system.

PV module peak power = 270 Wp

Vmp = 26.8 V

Number of modules in series = 4826.8

= 1.79 = 2

Number of modules = 9043.50 270

= 33.49 = 34

Number of modules in parallel =  NmNs

= 342 = 17

Total modules = 17 ×2 = 34

Peak power installed = 34 ×270

= 9180 Wp

CHARGE CONTROLLER SIZING

Isc = PpvVsys = 9043.50 48 = 188.51A

Applying a 25% safety factor:

Irated = 1.25×188.51

= 235.64 A

A charge controller with a current rating of at least 235.64 A is required.

CIRCUIT PROTECTION

Battery protection:

Iload​ = maximum load current

Ptotal = 2798.64 W

System voltage = 48V

Maximum load current:

Iload = Ptotal / Vsys

=2798.64/ 48 = 58.32 A

The battery fuse should satisfy:

Ifb > 1.1× Iload

= 1.1 × 58.32

= 100.84 A

The battery protection fuse should be rated above 100.84 A.

Battery bank protection:

Ifbb​ > MAX( Iload​ )

Ifbb​ = 58.32 A

A 63 A DC fuse is recommended for the battery bank protection, since it is above the calculated minimum current of 58.32 A and will safely protect the battery bank during fault conditions.

String protection:

Using module data style:

Isc = 9.4 A

The string fuse should satisfy:

1.5 Isc < If < 2 Isc

(1.5×9.4) < If < (2×9.4)

14.1 A < If ​< 18.8 A

A 16 A DC fuse is recommended for each PV string since it lies within the acceptable protection range of 14.1 A to 18.8 A.

Array protection:

The array fuse should satisfy:

1.5×Np×Isc < Ifa < 2×Np×Isc

(1.5×17×9.4) < Ifa < (2×17×9.4)

239.7 < Ifa < 319.6

A  300A DC fuse is recommended for the PV array protection, since it lies within the acceptable range of  239.7 A to 319.6 A and will safely protect the array during fault conditions.

CABLE PROTECTION

The cable size is selected based on the maximum current it will carry safely without overheating and with minimum voltage drop.

1. PV Array to Charge Controller

From the array protection calculation:

Iarray ≈ 350 A

A copper cable that can safely carry this current is required. Based on standard ampacity practice, a 185 mm² copper cable is suitable for this section.

2. Battery, Inverter, and Converter Connections

From the battery bank/load current:

Iload = 58.32 A

Using a factor of 25%

Idesign = 1.25×58.32 =72.9 A

A suitable cable for this current is 25 mm² copper cable.

CONCLUSION

The designed standalone PV system effectively meets the 35.51632 kWh/day load demand, with a required capacity of ≈9.043 kWp, supported by a 48 V, 1196.93 Ah

Ah battery bank and a 2 kVA inverter. Proper sizing of components and integration of protection schemes ensure system reliability, safety, and efficiency.

The close agreement between hand calculations and PVsyst results confirms the validity and practicality of the design, making it a sustainable and dependable solution for powering the lecture halls (A101,A102 and A103).